# N-1 Capacity Screening: Efficient vs. Manual Refactor Comparison

# Overview

This report compares two outputs of the Local N-1 Capacity Screening for substation ABHA4A: the manually refactored workbook and the efficient refactored script output. Both reach the same headline result, but the efficient version differs in several intermediate details.

# Headline Result (Agrees)

Both versions agree on the headline outcome and the binding row:

| Metric | Value (identical in both) |
| --- | --- |
| Estimated Additional Capacity | 1701.2 MW |
| Binding monitored element | ABHA4A-EXET41 OHL |
| Under N-1 outage of | ABHA4A-LAGA41 OHL |
| Base loading | 0.4% |
| Post-contingency loading | 8.13% |
| Headroom (binding row) | 1701.2 MW |

# Differences

## 1. Dropped Columns in the Efficient Version

Summary sheet omits “Test Increment (MW)” (value = 50), present as a column in the manual version.

Detail sheet omits “Loading at +50MW (%)” (manual column H). The efficient output therefore has no record of loading at the tested increment — only base and post-contingency loadings.

## 2. Sensitivity Sign Flipped

On the rows present in both files, the efficient version reports negative sensitivities where the manual reports positive:

| Outage to Monitored | Manual | Efficient |
| --- | --- | --- |
| EXET41 to LAGA41 | +0.041271 | -0.041271 |
| LAGA41 to EXET41 | +0.048123 | -0.048123 |
| Summary (binding) | +0.048123 | -0.048123 |

Headroom remains positive in both, indicating a sign-convention or bug difference rather than a different result. The intended convention should be confirmed.

## 3. Transformer-Monitored Loadings Zeroed Out

For the ElmTr3 (transformer) monitored rows, the manual version shows 61.47% base and post-contingency loading; the efficient version shows 0. Both still flag these rows as non-constraining, so the binding outcome is unaffected, but the efficient output has lost the actual transformer loading values.

## 4. Transformer Outage Skipped Rather Than Evaluated

Manual evaluates the ABHA11_Tx_1.ElmTr3 outage as two monitored rows (headrooms: non-constraining and 4761.2 MW, both non-binding).

Efficient collapses this to a single row labelled “Islanding outage — skipped” and never evaluates the monitored circuits. Because those rows were not binding, the final capacity is unchanged, but this is a genuine methodology difference (skip-as-islanding versus evaluate).

# Runtime

Both screenings ran on the same reduced network snapshot (1959 buses, 2913 branches, 185 couplers), so the timing difference reflects the screening method rather than the problem size. The efficient package finished in 9.5 s; the manual finite-difference run took 17.0 s — roughly 1.8 times slower, about 7.5 s of additional runtime on this single-substation case.

The gap follows directly from the methodology differences noted above. The manual version uses a finite-difference method, stepping load in 50 MW test increments and re-solving the network at each step, whereas the efficient version derives headroom analytically from the sensitivities. This is the same design choice that causes the efficient output to drop the “Test Increment” and “Loading at +50MW” columns (Difference 1): it never evaluates a discrete +50 MW operating point. The trade-off is speed against the intermediate detail and per-element evaluation lost in Differences 1 through 4. On a single substation the absolute saving is modest, but it would compound substantially across a larger candidate set.

# Conclusion

The refactor reproduces the final capacity and binding constraint correctly. However, it omits the +50MW test-increment columns, flips the sensitivity sign, zeroes transformer loadings, and skips the transformer outage as islanding. Items 2 through 4 should be checked before relying on the efficient script for other substations, where a skipped or zeroed element could be binding.