## Summary
Substation | Test Increment (MW) | Estimated Additional Capacity (MW) | Binding Monitored Element | Binding N-1 Contingency | Base Loading at Binding Element (%) | Post-Contingency Loading at Binding Element (%) | Sensitivity at Binding Element (%/MW) | Status | Bus Coupler State
ABHA4A | 50 | 1701.2 | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-EXET41_OHL_1.ElmLne | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-LAGA41_OHL_1.ElmLne | 0.4 | 8.13 | 0.048123 | OK | As-is

## Detail
Substation | Outage (Tripped Circuit) | Outage Class | Monitored Circuit | Monitored Class | Base Intact Loading (%) | Post-Contingency Loading (%) | Loading at +50MW (%) | Sensitivity (%/MW) | Headroom (MW) | Constraining? | Bus Coupler State
ABHA4A | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-EXET41_OHL_1.ElmLne | ElmLne | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-LAGA41_OHL_1.ElmLne | ElmLne | 7.32 | 6.98 | 9.04 | 0.041271 | 2011.7 | TRUE | As-is
ABHA4A | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-EXET41_OHL_1.ElmLne | ElmLne | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-ABHA11_Tx_1.ElmTr3 | ElmTr3 | 61.47 | 61.47 | 61.47 | 0 | Non-constraining | FALSE | As-is
ABHA4A | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-LAGA41_OHL_1.ElmLne | ElmLne | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-EXET41_OHL_1.ElmLne | ElmLne | 0.4 | 8.13 | 10.54 | 0.048123 | 1701.2 | TRUE | As-is
ABHA4A | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-LAGA41_OHL_1.ElmLne | ElmLne | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-ABHA11_Tx_1.ElmTr3 | ElmTr3 | 61.47 | 61.47 | 61.47 | 0 | Non-constraining | FALSE | As-is
ABHA4A | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-ABHA11_Tx_1.ElmTr3 | ElmTr3 | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-EXET41_OHL_1.ElmLne | ElmLne | 0.4 | 4.99 | 3.63 | -0.02713 | Non-constraining | TRUE | As-is
ABHA4A | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-ABHA11_Tx_1.ElmTr3 | ElmTr3 | \solomonj.IntUser\Auto_Network_Model_2027.IntPrj\Network Model.IntPrjfolder\Network Data.IntPrjfolder\Grid.ElmNet\ABHA\ABHA4A-LAGA41_OHL_1.ElmLne | ElmLne | 7.32 | 4.28 | 5.18 | 0.018004 | 4761.2 | TRUE | As-is